## Cover
Business Energy Solutions
2026 Rebate Application
Prescriptive Measures for Existing Facilities
HVAC System Test and Repair
Submit application to:
UniSource Business Energy Solutions
Tel: 1-866-540-4315
UniSourceBES@franklinenergy.com
Application Process
1. Submit a Pre-Notification Application.
2. Install the qualified technology.
3. Submit a complete, signed Final Application with all documentation.
4. Receive incentive check within 6 weeks of Final Application approval.
Last Modified: 9/1/2026
The Commercial Energy Solutions Program is paid for by UniSource Energy Services customers and approved by the Arizona Corporation Commission.

## HVAC System Test Repair
UES - Prescriptive Application | [8 empty] | For HELP hover mouse over light grey shading for additional information. Yellow shaded cells indicate Data Entry.
System Test and Repair Worksheet | [5 empty] | 2026-09-01
Project Name: | [8 empty] | UES Account #:
System Test and Repair Incentives
|  |  | Measure | [5 empty] | Base Incentive per Unit
|  |  | Coil Clean (CC) | [5 empty] | 50
|  |  | Refrigerant Charge (RCA) | [5 empty] | 50
|  |  | Advanced Diagnostic Tune Up (CC+RCA) | [5 empty] | 100 | [11 empty] | System_Test_and_Repair
|  |  | Economizer Repair (ECON) | [5 empty] | 110 | [11 empty] | Coil Clean (CC) | Heat Pump
|  |  | Duct Test and Repair (DTR) | [5 empty] | 390 | [11 empty] | Refrigerant Charge (RCA) | AC Only
|  |  | Any Combination of Measures | [5 empty] | Sum of Base incentives | [11 empty] | Advanced Diagnostic Tune Up (CC+RCA)
Economizer Repair (ECON)
Duct Test and Repair (DTR)
Installed Measures
Measure |  | Unit Description (RTU1,3) |  |  | ADTU |  | ECON | DTR | AC or Heat Pump | SEER or EER | Unit Count | Size (Tons) | No. of Circuits (ADTU+ only) | Base Incentive (per Unit) | Capped Incentive Amount
[5 empty] | CC | RCA | [10 empty] | Type | Measure Name | Complete | Increm Cost Cap per unit
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 |  |  | Incremental Cost Cap% | 50%
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 |  |  | Size For Incentive (Tons) | 5
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | Look up Table
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | FALSE,FALSE,FALSE,FALSE | MeasureSize Category | Base Incentive (per Unit) | Efficiency Incentive (per Unit) | Incremental Cost (per Ton) | Measure ID | PrescriptiveMeasureDescription | Coin Demand (kW) | Total Annual Energy | Incremental Cost ($) | O&M Cost ($) | SCT Benefits | SCT Net Benefits | SCT B/C
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | TRUE,FALSE,FALSE,FALSE | Coil Clean (CC) | 50 |  | 20 | 2212796502 | C&I Comprehensive HVAC System Test and Repair - AC Coil Clean (CC) | 0.047925 | 203.7264 | 0 | 0 | 37.66 | 10.4 | 1.4
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | FALSE,TRUE,FALSE,FALSE | Refrigerant Charge (RCA) | 50 |  | 20 | 2212796501 | C&I Comprehensive HVAC System Test and Repair - AC Refrigerant Charge and Airflow (RCA) | 0.064001 | 272.065 | 0 | 0 | 50.29 | 20.6 | 1.7
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | TRUE,TRUE,FALSE,FALSE | Advanced Diagnostic Tune Up (CC+RCA) | 100 |  | 40 | 2212796498 | C&I Comprehensive HVAC System Test and Repair - AC (CC+RCA) | 0.11193 | 475.7914 | 24.7196 | 0 | 87.95 | 31 | 1.5
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | FALSE,FALSE,TRUE,FALSE | Economizer Repair (ECON) | 110 |  | 44.46 | 2212796499 | C&I Comprehensive HVAC System Test and Repair - AC Economizer (ECON) | 0.07583 | 322.3519 | 44.4602 | 0 | 59.59 | 3.64 | 1.1
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | FALSE,FALSE,FALSE,TRUE | Duct Test and Repair (DTR) | 390 |  | 157.33 | 2212796500 | C&I Comprehensive HVAC System Test and Repair - AC Duct Test and Repair (DTR) | 0.044204 | 187.9105 | 157.33 | 0 | 98.09 | -65.94 | 0.6
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | TRUE,FALSE,TRUE,FALSE | Coil Clean (CC)Economizer Repair (ECON) | 160 |  | 64.46 | 2212796509 | C&I Comprehensive HVAC System Test and Repair - HP Coil Clean (CC) | 0.055601 | 236.3573 | 0 | 0 | 43.69 | 15.27 | 1.5
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | TRUE,FALSE,FALSE,TRUE | Coil Clean (CC)Duct Test and Repair (DTR) | 440 |  | 177.33 | 2212796508 | C&I Comprehensive HVAC System Test and Repair - HP Refrigerant Charge and Airflow (RCA) | 0.074252 | 315.6418 | 0 | 0 | 58.35 | 27.1 | 1.9
System Test and Repair |  |  |  |  | FALSE | FALSE | FALSE | FALSE | [8 empty] | FALSE,FALSE,FALSE,FALSE | MeasureSize Category |  | 0 | TRUE,FALSE,TRUE,TRUE | Coil Clean (CC)Economizer Repair (ECON)Duct Test and Repair (DTR) | 550 |  | 221.79 | 2212796505 | C&I Comprehensive HVAC System Test and Repair - HP (CC+RCA) | 0.12985 | 551.9991 | 24.7196 | 0 | 102.04 | 42.37 | 1.7
[21 empty] | FALSE,TRUE,TRUE,FALSE | Refrigerant Charge (RCA)Economizer Repair (ECON) | 160 |  | 64.46 | 2212796506 | C&I Comprehensive HVAC System Test and Repair - HP Economizer (ECON) | 0.087976 | 373.9831 | 44.4602 | 0 | 69.13 | 11.35 | 1.2
Project Completion Date | [13 empty] | Total: | 0 | [5 empty] | FALSE,TRUE,FALSE,TRUE | Refrigerant Charge (RCA)Duct Test and Repair (DTR) | 440 |  | 177.33 | 2212796507 | C&I Comprehensive HVAC System Test and Repair - HP Duct Test and Repair (DTR) | 0.10013 | 425.632 | 157.33 | 0 | 222.18 | 49.68 | 1.3
[16 empty] | Rebates cannot exceed 50% of the incremental measure cost. |  |  |  |  | FALSE,TRUE,TRUE,TRUE | Refrigerant Charge (RCA)Economizer Repair (ECON)Duct Test and Repair (DTR) | 550 |  | 221.79
[21 empty] | TRUE,TRUE,TRUE,FALSE | Advanced Diagnostic Tune Up (CC+RCA)Economizer Repair (ECON) | 210 |  | 84.46
Measure Specifications | [20 empty] | TRUE,TRUE,FALSE,TRUE | Advanced Diagnostic Tune Up (CC+RCA)Duct Test and Repair (DTR) | 490 |  | 197.33
All work shall be performed in accordance with all applicable professional standards and comply with all applicable federal, state, and local laws, ordinances,codes and regulations. | [20 empty] | TRUE,TRUE,TRUE,TRUE | Advanced Diagnostic Tune Up (CC+RCA)Economizer Repair (ECON)Duct Test and Repair (DTR) | 600 |  | 241.79
[21 empty] | FALSE,FALSE,TRUE,TRUE | Economizer Repair (ECON)Duct Test and Repair (DTR) | 500 | 0 | 201.79
Coil Clean (CC) -Must not have been cleaned within the past three years. Cleaning must be done by a qualified technician following standard practices outlined in the Checklist tab in this worksheet. Belt replacement (if applicable), air filter change, condenser coil cleaning with a non-acidic chemical, evaporator coil cleaning (as needed), cleaning condensate drain lines, electrical connections checked and tightened
Refrigerant Charge and Airflow (RCA) - Unit must be 20% above or below manufacturer specifications to qualify. If during inspection refrigerant charge is found to be more than 20% above or below manufacturer specifications, record installed refrigerant amount. Consists of an air conditioning equipment performance test with program approved specialized test equipment, tune-up with repairs and a test-out. Outdoor temperature must be 55 degrees F or higher for systems with R410A and 60 degree F or higher for systems with R22 during the tune-up and repair procedure. The indoor return air plenum temperature must be 70 degrees F or higher at the end of the test cycle.
Advanced Diagnostic Tune-Up (CC+RCA)- Coil Clean and Refrigerant charge and air flow verification shown above, and any repairs required to bring the system back to the manufacturer's specifications.
See chart below for criteria:
| System Type |  |  | Criteria
| For Fixed Orifice Systems |  |  | +/- 5 deg F of Target Superheat & + 3 deg F / -5 deg F of Target Temp Split
| For Systems with TXV |  |  | +/- 5 deg F of Target Subcooling & + 3 deg F / -5 deg F of Target Temp Split
| All |  |  | Air flow > 326 < 450 CFM per ton or + 3 deg F / -5 deg F of Target Temp Split between supply and return air
Economizer Repair (ECON) - If an economizer does not open or close under simulated cold or hot outdoor temperatures, a repair must be completed.
Duct Test & Repair (DTR)- uses diagnostic equipment to measure & repair duct leakage. The first step is to perform a "Duct Leakage Test In" to determine total leakage. If the system leakage is greater than 60 CFM/ton the ducts shall be sealed until the duct leakage is less than 60 CFM/ton or until leakage is reduced by 20% of total fan flow. The "Duct Leakage Test Out" shall be measured after sealing or repairing duct system using the same procedure as the initial test.
Documentation Requirements - System size (tons), nameplate SEER or EER and age (if available), nameplate refrigerant quantity (lbs.), target and actual superheat or subcool temperatures from all tests, amount of refrigerant added or removed, target and actual for supply and return temperature differentials from all tests, air flow CFM from all tests, duct leakage CFM from all tests, economizer position at simulated outside hot and cold temperatures.
Participation Requirements - To participate in the HVAC Testing & Repair program units must have a capacity of 3 tons or greater and contractors must be an approved contractor in the UES Commercial Energy Solutions Program.
Note on T17: Enter the number of refrigerant circuits. Applies to Measure Type including ADTU only.
Note on Z18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No of Circuits is not a hard stop
Note on AA18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Set based on cell AF22

## Photo Documentation
UES Test and Repair Photo Documentation
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:
Unit Name: | Measure Name:

## Checklist
Custom Name |  | Date:
Address |  | Technician
City/State/Zip |  | Job#
Equipment ID |  | Critical Repairs:
Manufacturer |  | ________________________________________________
Model Number |  | ________________________________________________
Serial Number |  | ________________________________________________
Refrigerant | Type | Non-Critical Recommendations:
| Qty (lbs) | ________________________________________________
Filters | Size | ________________________________________________
| Qty | ________________________________________________
Required for Rebate
Coil Clean |  |  | Pre
FALSE | Condenser coil cleaning with a non-acidic chemical |  | Suction Pressure |  | RAT
FALSE | Evaporator coil cleaning (as needed) |  | Head Pressure |  | SAT
FALSE | Clean condensate drain line |  | Subcooling |  | Amb Temp
FALSE | Clean/Straighten indoor and outdoor fan blades |  | Superheat |  | Δ T | 0
FALSE | Repair damaged insulation – suction line
FALSE | Change air filter (if needed) |  | Post
RCA |  |  | Suction Pressure |  | RAT
FALSE | Refrigerant charge diagnosis and recharge system to OEM specifications |  | Head Pressure |  | SAT
FALSE | Identify and repair leaks if refrigerant charge is low |  | Subcooling
FALSE | Measure and record refrigerant pressures |  | Superheat |  | Δ T | 0
FALSE | Measure and record temperature drop at indoor coil
FALSE | Refrigerant charge above or below >20% and charged to OEM specifications
Advance Diagnostic Tune-Up |  |  | Refrigerant Oz |  | Notes
FALSE | Outdoor air temperature above 55 ° |  | Factory Charge
FALSE | +/- 5 deg F of Target Superheat & + 3 deg F / -5 deg F of Target Temp Split |  | Current Charge
FALSE | Indoor return air plenum above 70 ° |  | Added Charge
FALSE | Air flow between > 326 <450 CFM/ton |  | Charge Correction | 0%
Economizer
FALSE | Programmed to meet ASHRAE 90.1 changeover setpoints
FALSE | Replace Damper Motor (if needed) |  | Control Type
FALSE | Repair Damper Linkage (if needed) |  | High-Limit Setpoint
FALSE | Repair Economizer Wiring |  | ASHRAE Setpoint
FALSE | Reduce Over Ventilation
FALSE | Replace Economizer Sensor
FALSE | Replace Economizer Control
FALSE | Non-Functioning Economizer made operational
Duct Test and Repair |  |  | Total Leakage
FALSE | Determine total leakage |  | Pre System CFM
FALSE | Greater than 60CFM/ton |  | Post System CFM
FALSE | Sealed until the duct leakage is less than 60 CFM/ton or until leakage is reduced by 20% of total fan flow
Notes

## (CC+RCA) Tasking (hidden)
Date of Service
Done | Task | Notes
Clean condensate drain line
Clean outdoor coil and straighten fins
Clean indoor and outdoor fan blades
Clean indoor coil with spray-on cleaner and straighten fins
Repair damaged insulation – suction line
Change air filter
Measure and record blower amp draw
Refrigerant charge diagnosis and recharge system to OEM specifications
Identify and repair leaks if refrigerant charge is low
Measure and record refrigerant pressures
Measure and record temperature drop at indoor coil
Refrigerant charge off >20% and charged to OEM specifications

## Testing Summary (hidden)
Location: |  |  |  |  | C&I HVAC Test and Repair
[7 empty] | Post Conditions | [10 empty] | Potential Incentive
Unit | Tons | Brand | Model | Type (AC/HP) | Rated SEER EER | Refrigerant | Suction Pressure | Head Pressure | Sub Cooling | Super Heat | Δ T | Ambient Temp | Factory Charge Oz | Added Charge Oz | Charge Correction | Target Superheat | Target Δ Temp | CC Incentive | RCA Incentive | Notes
RTU1-1 | 3.5 | Rheem | RQNJ-A042 | HP | 14 | R-410A | 78 | 230 | 9 | 18 | 15 | 92 | 100 | 21 | 21% | Concern | PASS |  | $$ | Example
Note on K3: Exected Super Heat between 5 and 15
Note on L3: Expected Δ air flow between 15 and 23
Note on Q3: Typical range: 8–12°F for TXV systems. Low Subcooling (<8°F) → Possible undercharge or metering device issue. High Subcooling (>15°F) → Possible overcharge or restricted metering device. Superheat too high (>15°F) → Undercharge or airflow issue. Superheat too low (<5°F) → Overcharge or flooding TXV.
Note on R3: Normal range: 18–22°F. Determined by coil design and airflow (usually 400 CFM per ton). High ΔT (>22°F) → low airflow; Low ΔT (<16°F) → high airflow or low refrigerant charge.

## Criteria (hidden)
R-410A (Cooling Mode) | ⚠ Notes:
Suction Pressure: 118–135 psi (≈ 40–50°F saturation) | Higher ΔT (>22°F) → Possible low airflow (dirty filter, blower issue).
Head Pressure: 360–410 psi (≈ 100–120°F saturation) | Low Subcooling (<8°F) → Possible undercharge or metering device issue.
Subcooling: 8–12°F (manufacturer-specific) | High Subcooling (>15°F) → Possible overcharge or restricted metering device.
Superheat: 8–12°F (TXV systems) | Superheat too high (>15°F) → Undercharge or airflow issue.
ΔT (Temp Split): 18–22°F | Superheat too low (<5°F) → Overcharge or flooding TXV.
Return Air Temp: ~75°F
Supply Air Temp: ~53–57°F
Ambient Air Temp: 90–95°F (affects head pressure) | Refrigerant | Suction Min | Suction Max | Head Min | Head Max | SC Min | SC Max | SH Min | SH Max | ΔT Min | ΔT Max | Notes
| R-410A | 118 | 135 | 360 | 410 | 8 | 12 | 8 | 12 | 18 | 22 | ~90–95°F ambient, TXV
| R-22 | 68 | 82 | 225 | 250 | 8 | 12 | 8 | 12 | 18 | 22 | ~90–95°F ambient, TXV
R-22 (Cooling Mode) | [5 empty] | System Type |  | SH Min | SH Max | ΔT Min | ΔT Max
[6 empty] | R-410A |  | 5 | 15 | 15 | 23
Suction Pressure: 68–82 psi (≈ 40–50°F saturation) | [5 empty] | R-22 |  | 5 | 15 | 15 | 23
Head Pressure: 225–250 psi (≈ 100–115°F saturation)
Subcooling: 8–12°F | R-410A psi | R-410A Sat °F | R-22 psi | R-22 Sat °F |  |  |  |  | System Type | Criteria
Superheat: 8–12°F | 100 | 37 | 60 | 34 |  |  |  |  | For Fixed Orifice Systems | +/- 5 deg F of Target Superheat & + 3 deg F / -5 deg F of Target Temp Split
ΔT (Temp Split): 18–22°F | 110 | 41 | 68 | 40 |  |  |  |  | For Systems with TXV | +/- 5 deg F of Target Subcooling & + 3 deg F / -5 deg F of Target Temp Split
Return Air Temp: ~75°F | 118 | 44 | 75 | 44 |  |  |  |  | All | Air flow > 326 < 450 CFM per ton or + 3 deg F / -5 deg F of Target Temp Split between supply and return air
Supply Air Temp: ~53–57°F | 125 | 47 | 82 | 48
Ambient Air Temp: 90–95°F | 135 | 50 | 90 | 52
| 350 | 100 | 210 | 98
| 360 | 103 | 225 | 104
| 380 | 110 | 240 | 110
| 400 | 116 | 255 | 116
1. Pressure Ranges | 420 | 122 | 270 | 122
Each refrigerant has a unique pressure-temperature relationship (PT chart).
For example:
R-410A at 40°F saturation = ~118 psi; at 50°F = ~135 psi.
R-22 at 40°F saturation = ~68 psi; at 50°F = ~82 psi.
These pressures correspond to the evaporator coil temperature during cooling mode.
Head pressure is based on condensing temperature, typically 20–30°F above ambient.
So at 95°F ambient, condensing temp ≈ 115°F →
R-410A ≈ 360–410 psi
R-22 ≈ 225–250 psi.
2. Subcooling
Subcooling = difference between liquid line temperature and saturation temperature at condenser pressure.
Manufacturers specify target subcooling (usually 8–12°F for TXV systems).
Ensures enough liquid refrigerant reaches the metering device without flash gas.
3. Superheat
Superheat = difference between suction line temperature and saturation temperature at evaporator pressure.
Typical range: 8–12°F for TXV systems.
Ensures no liquid refrigerant returns to the compressor.
4. Temperature Split (ΔT)
ΔT = Return Air Temp – Supply Air Temp.
Normal range: 18–22°F.
Determined by coil design and airflow (usually 400 CFM per ton).
High ΔT (>22°F) → low airflow; Low ΔT (<16°F) → high airflow or low refrigerant charge.